Relay Oscillography Event Report

| Station | Test Substation |
| --- | --- |
| Device / Relay ID | SEL-421-Relay |
| Location / Substation | North Substation 115kV |
| Relay / Device Type | SEL-421 Distance Relay |
| Recording Start | 2024-01-01 00:00:00.000 |
| Trigger Time | 2024-01-01 00:00:00.050 |
| Duration | 199.5 ms |
| Sample Rate | 1920 Hz (32 samples/cycle) |
| Channels | 7 analog / 4 digital |
| COMTRADE Revision | 1999 |
| Data Format | ASCII |

Event Operations Summary

| Parameter | Measured / Detail | Status |
| --- | --- | --- |
| Fault Type | Double Line-to-Ground (LLG) | Classified |
| Fault Inception | 50.52 ms (+0.5 ms from trigger) | Detected |
| Elements Operated | 51P, 50G, TRIP | Operated |
| Trip Time | 130.21 ms (+80.2 ms from trigger) [TRIP] | Tripped |
| Fault Clearing Time | 79.7 ms (inception → trip) | 80 ms |
| Relay Operate Time (Trip Delay) | 79.7 ms (IEEE time-delay grading reference: varies by coordination) | 80 ms |

Peak Measured Quantities

| Channel | Peak Magnitude | Units | Type |
| --- | --- | --- | --- |
| IA | 960.00 | A | Current |
| IB | 139.69 | A | Current |
| IC | 139.69 | A | Current |
| IN | 960.00 | A | Current |
| VAN | 6927.96 | V | Voltage |
| VBN | 7258.91 | V | Voltage |
| VCN | 7258.91 | V | Voltage |

Waveform Record

Figure: Three-phase currents, voltages, and digital status.  Red dashed line = fault inception.  Green dotted line = trip.  Orange line = trigger.

Digital Operations Log

| Channel | Event | Time (ms) | Rel. Trigger (ms) |
| --- | --- | --- | --- |
| 51P | ASSERT (0→1) | 50.00 | -0.00 |
| 50G | ASSERT (0→1) | 51.04 | +1.04 |
| TRIP | ASSERT (0→1) | 130.21 | +80.21 |

Analysis Notes

Fault classification:  Double Line-to-Ground. Two phases faulted to ground. Often initiated by a single conductor contacting ground and subsequently involving an adjacent phase.

DC Offset:

IA: DC component ≈ 309.7 A  |  time constant τ ≈ 927.8 ms. DC offset is caused by the point-on-wave of fault inception relative to the voltage zero crossing. Full offset (50% of peak current added as DC) is worst-case for breaker interruption duty.

IN: DC component ≈ 338.8 A  |  time constant τ ≈ 745.0 ms. DC offset is caused by the point-on-wave of fault inception relative to the voltage zero crossing. Full offset (50% of peak current added as DC) is worst-case for breaker interruption duty.

Symmetrical Sequence Components (post-fault, one-cycle average):

I₁ (Positive) = 312.1 A  |  I₂ (Negative) = 184.9 A  |  I₀ (Zero) = 184.5 A

Negative-to-positive ratio: 59%  (< 5% expected for balanced 3-phase faults; significant I₂ indicates phase-to-phase or ground fault involvement). Zero-to-positive ratio: 59%  (significant I₀ confirms ground fault path).

Prepared by:

Jane Smith

Protection Engineer