Relay Oscillography Event Report

| Station | Maple Ave Feeder |
| --- | --- |
| Device / Relay ID | SEL-351R-Recloser |
| Location / Substation | Maple Ave Feeder — Bay 3 |
| Relay / Device Type | SEL-351R Recloser Controller |
| Recording Start | 2026-06-01 14:22:15.000 |
| Trigger Time | 2026-06-01 14:22:15.050 |
| Duration | 3199.5 ms |
| Sample Rate | 1920 Hz (32 samples/cycle) |
| Channels | 7 analog / 6 digital |
| COMTRADE Revision | 1999 |
| Data Format | ASCII |

Event Operations Summary

| Parameter | Measured / Detail | Status |
| --- | --- | --- |
| Fault Type | Single Line-to-Ground (SLG) | Classified |
| Fault Inception | 50.52 ms (+0.5 ms from trigger) | Detected |
| Elements Operated | 50P, TRIP, 79, 52A, 51P, LOCK | Operated |
| Trip Time | 66.14 ms (+16.1 ms from trigger) [TRIP] | Tripped |
| Fault Clearing Time | 15.6 ms (inception → trip) | 16 ms |
| Relay Operate Time (Trip Delay) | 15.6 ms (IEEE time-delay grading reference: varies by coordination) | 16 ms |

Peak Measured Quantities

| Channel | Peak Magnitude | Units | Type |
| --- | --- | --- | --- |
| IA | 720.00 | A | Current |
| IB | 99.78 | A | Current |
| IC | 99.78 | A | Current |
| IN | 720.00 | A | Current |
| VAN | 10179.94 | V | Voltage |
| VBN | 10970.74 | V | Voltage |
| VCN | 10970.74 | V | Voltage |

Waveform Record

Figure: Three-phase currents, voltages, and digital status.  Red dashed line = fault inception.  Green dotted line = trip.  Orange line = trigger.

Recloser / Feeder Relay Operations

Outcome:  LOCKED OUT (permanent fault)

Fault is PERMANENT — device locked out.  A line patrol or feeder sectionalizing is required to locate and clear the fault.

Operation Sequence

| Shot | Element | Type | Operate Time (ms) | Dead Time (ms) | Outcome |
| --- | --- | --- | --- | --- | --- |
| 1 | 50P | FAST | 16.1 | 500 | RECLOSED |
| 2 | 51P | SLOW | 340.1 | 2000 | RECLOSED |
| 3 | 50P | FAST | 16.1 | N/A | LOCKOUT |

Fault Location Estimate

Faulted phase: A.  Estimated distance: ~3.7 miles from the substation.  Fault current: 487 A RMS.  Apparent fault impedance: 1.48 Ω at 0.400 Ω/mile.  Accuracy: ±20–30% without arc resistance / load compensation.

Voltage Recovery After Reclose

Shot 1: Voltage did NOT recover to 90% within the observation window (post-reclose level: 12%).  Possible reclose into a still-present fault.

Shot 2: Voltage did NOT recover to 90% within the observation window (post-reclose level: 0%).  Possible reclose into a still-present fault.

Digital Operations Log

| Channel | Event | Time (ms) | Rel. Trigger (ms) |
| --- | --- | --- | --- |
| 50P | ASSERT (0→1) | 50.00 | -0.00 |
| TRIP | ASSERT (0→1) | 66.14 | +16.14 |
| 50P | RELEASE (1→0) | 66.14 | +16.14 |
| 52A | RELEASE (1→0) | 66.14 | +16.14 |
| TRIP | RELEASE (1→0) | 566.14 | +516.14 |
| 79 | ASSERT (0→1) | 566.14 | +516.14 |
| 52A | ASSERT (0→1) | 566.14 | +516.14 |
| 51P | ASSERT (0→1) | 570.31 | +520.31 |
| 79 | RELEASE (1→0) | 576.04 | +526.04 |
| TRIP | ASSERT (0→1) | 910.42 | +860.42 |
| 51P | RELEASE (1→0) | 910.42 | +860.42 |
| 52A | RELEASE (1→0) | 910.42 | +860.42 |
| TRIP | RELEASE (1→0) | 2910.42 | +2860.42 |
| 79 | ASSERT (0→1) | 2910.42 | +2860.42 |
| 52A | ASSERT (0→1) | 2910.42 | +2860.42 |
| 50P | ASSERT (0→1) | 2914.06 | +2864.06 |
| 79 | RELEASE (1→0) | 2920.31 | +2870.31 |
| TRIP | ASSERT (0→1) | 2930.21 | +2880.21 |
| 52A | RELEASE (1→0) | 2930.21 | +2880.21 |
| LOCK | ASSERT (0→1) | 2930.21 | +2880.21 |

Analysis Notes

Fault classification:  Single Line-to-Ground (A-phase to ground is the most common type, accounting for approximately 70–80% of all transmission faults).

DC Offset:

IA: DC component ≈ 251.6 A  |  time constant τ ≈ 759.3 ms. DC offset is caused by the point-on-wave of fault inception relative to the voltage zero crossing. Full offset (50% of peak current added as DC) is worst-case for breaker interruption duty.

IB: DC component ≈ 5.1 A  |  time constant τ ≈ 5788.2 ms. DC offset is caused by the point-on-wave of fault inception relative to the voltage zero crossing. Full offset (50% of peak current added as DC) is worst-case for breaker interruption duty.

IC: DC component ≈ -5.7 A  |  time constant τ ≈ 5108.7 ms. DC offset is caused by the point-on-wave of fault inception relative to the voltage zero crossing. Full offset (50% of peak current added as DC) is worst-case for breaker interruption duty.

IN: DC component ≈ 274.8 A  |  time constant τ ≈ 615.6 ms. DC offset is caused by the point-on-wave of fault inception relative to the voltage zero crossing. Full offset (50% of peak current added as DC) is worst-case for breaker interruption duty.

Symmetrical Sequence Components (post-fault, one-cycle average):

I₁ (Positive) = 149.9 A  |  I₂ (Negative) = 92.0 A  |  I₀ (Zero) = 87.5 A

Negative-to-positive ratio: 61%  (< 5% expected for balanced 3-phase faults; significant I₂ indicates phase-to-phase or ground fault involvement). Zero-to-positive ratio: 58%  (significant I₀ confirms ground fault path).

Prepared by:

Jane Smith

Protection Engineer